## Slide 1
DEEP SEA ELECTRONICS PLC
Highfield House, Hunmanby Industrial Estate, Hunmanby, North Yorkshire YO14 0PH England
TELEPHONE +44 (0) 1723 890099 FASCIMILE +44 (0) 1723 890099 EMAIL sales@deepseaplc.com
www.deepseaplc.com
DSEGENCOMM PROTOCOL
DSE7200, DSE7300, DSE7400, DSE8600, DSE8700, DSE8800 series
GENCOMM ALARMS
Notes: DSE controllers fitted with RS232 / RS485 ports utilise modbus RTU protocol over twisted pair cable.
DSE controllers with integral Ethernet ports utilise modbus TCP over CAT5 cable.

## Slide 2
www.deepseaplc.com
OVERALL STATUS
For alarm status, read page 3, register 6
This contains a bit field of status information :
Register offset | Name | Minimum value | Maximum value | Scaling factor | Units | Bits/ sign
0 | Manufacturer code | 0 | 65534 | 1 |  | 16
1 | Model number | 0 | 65534 | 1 |  | 16
2-3 | Serial number | 0 | 999999999 | 1 |  | 32
4 | Control mode | 0 | 65535 | 1 |  | 16
5 | Unimplemented | 0xFFFF | 0xFFFF |  |  | 16
6 | Control unit not configured | No | Yes |  |  | 16/16
 | Unimplemented | 0 | 0 |  |  | 15/16
 | Control unit failure | No | Yes |  |  | 14/16
 | Shutdown alarm active | No | Yes |  |  | 13/16
 | Electrical trip alarm active | No | Yes |  |  | 12/16
 | Warning alarm active | No | Yes |  |  | 11/16
 | Telemetry alarm flag | Not active | Active |  |  | 10/16
 | Satellite telemetry alarm flag | Not active | Active |  |  | 9/16
 | No font file | No | Yes |  |  | 8/16
 | Unimplemented | 0 | 0 |  |  | 1/16-7/16
Notes: Here are the first six registers in Page 3 (Hex Address 0300 – Address 03FF)
Register 6 (hex 0306) contains status bits about the state of the alarms in the controller (0 = no alarm, 1=alarm present)
Now we know if there are any alarms present, we have to read to see which alarm(s) are active, there may be more than one!

## Slide 3
www.deepseaplc.com
ACTIVE ALARMS
To find which alarms are active, read page 153 for unnamed (user configured) alarms and page 154 for named (pre-configured) alarms. :
Register offset | Name | Minimum value | Maximum value | Bits/ Sign
0 | Number of named alarms | 61 | 128 | 16
1 | Emergency stop | 0 | 15 | 13/16-16/16
 | Low oil pressure | 0 | 15 | 9/16-12/16
 | High coolant temperature | 0 | 15 | 5/16-8/16
 | High oil temperature | 0 | 15 | 1/16-4/16
2 | Under speed | 0 | 15 | 13/16-16/16
 | Over speed | 0 | 15 | 9/16-12/16
 | Fail to start | 0 | 15 | 5/16-8/16
 | Fail to come to rest | 0 | 15 | 1/16-4/16
Notes: Each register contains the status of four alarms, each alarm’s status given in a four bit value (0-15)

## Slide 4
www.deepseaplc.com
ALARM CONDITIONS
Condition | Meaning | Displayed string
0 | Disabled digital input | None
1 | Not active alarm | None
2 | Warning alarm | Active string
3 | Shutdown alarm | Active string
4 | Electrical trip alarm | Active string
5-7 | Reserved | 
8 | Inactive indication (no string) | None
9 | Inactive indication (displayed string) | Inactive string
10 | Active indication | Active string
11-14 | Reserved | 
15 | Unimplemented alarm | None
Notes: Each register contains the status of four alarms, each alarm’s status given in a four bit value (0-15)
The value returned for a specific alarm, tells what kind of alarm it is.

## Slide 5
www.deepseaplc.com
GENCOMM ALARMS EXAMPLE
0 0 0 1 1 1 1 1 0 0 1 0 0 0 1 1
Binary value | Decimal | Alarm Status
0001 | 1 | No alarm present
0010 | 2 | Warning alarm
0011 | 3 | Shutdown alarm
0100 | 4 | Electrical Trip alarm
1111 | 15 | Unimplemented alarm in this controller
Notes: Each register contains the status of four alarms, each alarm’s status given in a four bit value (0-15)
The value returned for a specific alarm, tells what kind of alarm it is.
Split the binary value into the four smaller packets and convert them to decimal to compare them with the Alarm condition codes table from the Gencomm document.
An unimplemented alarm means that the controller does not support this alarm, or it has been disabled in the module’s configuration.

## Slide 6
www.deepseaplc.com
GENCOMM ALARMS EXAMPLE
0 0 0 1 1 1 1 1 0 0 1 0 0 0 1 1
To check a specific alarm ‘programmatically’ we need to check specific bits.
We can do this using ‘bit shifting’ and ‘bit masking’
Notes: Each register contains the status of four alarms, each alarm’s status given in a four bit value (0-15)
The value returned for a specific alarm, tells what kind of alarm it is.
Split the binary value into the four smaller packets and convert them to decimal to compare them with the Alarm condition codes table from the Gencomm document.
An unimplemented alarm means that the controller does not support this alarm, or it has been disabled in the module’s configuration.

## Slide 7
www.deepseaplc.com
GENCOMM ALARMS EXAMPLE
0 0 0 1 1 1 1 1 0 0 1 0 0 0 1 1
Shift Right >> 4 bits
0 0 0 0 0 0 0 1 1 1 1 1 0 0 1 0
For example to test the second set of four bits we first shift the value right four bits.

## Slide 8
www.deepseaplc.com
GENCOMM ALARMS EXAMPLE
0 0 0 1 1 1 1 1 0 0 1 0 0 0 1 1
Shift Right >> 4 bits
0 0 0 0 0 0 0 1 1 1 1 1 0 0 1 0
For example to test the second set of four bits we first shift the value right four bits.

## Slide 9
www.deepseaplc.com
GENCOMM ALARMS EXAMPLE
0 0 0 1 1 1 1 1 0 0 1 0 0 0 1 1
Shift Right >> 4 bits
0 0 0 0 0 0 0 1 1 1 1 1 0 0 1 0
For example to test the second set of four bits we first shift the value right four bits.

## Slide 10
www.deepseaplc.com
GENCOMM ALARMS EXAMPLE
0 0 0 0 0 0 0 1 1 1 1 1 0 0 1 0
AND
0 0 0 0 0 0 0 0 0 0 0 0 1 1 1 1
=
0 0 0 0 0 0 0 0 0 0 0 0 0 0 1 0
and perform a ‘logical AND’ to mask out the most significant 12 bits.

## Slide 11
www.deepseaplc.com
GENCOMM ALARMS EXAMPLE
0 0 0 0 0 0 0 0 0 0 0 0 0 0 1 0
Now we can test the number against the table of alarm status’s.
0010 (Binary) = 2 (Decimal) = Warning alarm

## Slide 12
www.deepseaplc.com
GENCOMM ALARMS EXAMPLE
0 0 0 0 0 0 0 0 0 0 0 0 0 0 1 0
In the C language this is performed by
AlarmStatus = (value >> 4) & 15 ;
Shift right by 4 bits
Logical AND