(The register address is obtained from the formula:

register_address=page_number*256+register_offset. ( +1 )

To read the Engine Speed from the above register, the MODBUS master device needs to read the data in two registers and then combine the data from the Most Significant Bit and the Least Significant Bit.

MSB address in Decimal = (166 * 256) + 2 = 42498

LSB address in Decimal = (166 * 256) + 3 = 42499)

Page 3 example: Generating Set Status Information

Control mode:

what you have to do is to look to the page 3 and then read the register offset 4 which indicate the control mode (there should be a value).

Now this value will represent one of these modes in below table.

Ex: if you find in register offset 4 a value 2 .. this means it is in the manual mode and so on.

engine operation

The same is for engine operation state:

Page 4 example: Basic Instrumentation

you have to just read the register offset direct follow the above equation as example bellow ( I am using Modscan software )

| Register offset | Name | Register address |
| --- | --- | --- |
| 0 | Oil pressure | 1025 |
| 1 | Coolant temperature | 1026 |
| 2 | Oil temperature | 1027 |
| 3 | Fuel level | 1028 |
| 4 | Charge alternator voltage | 1029 |
| 5 | Engine Battery voltage | 1030 |
| 6 | Engine speed | 1031 |

In above example (for my desk simulator):

Coolant temp 58

Oil Temp 32767

Fuel level 82%

Chrge Alt 0

Engine battery 26.9

Engine speed 1432

Ans so on … (These are just my simulator numbers, and it is just an example)

Page 8 example: Alarm Conditions

In page 8, register offset 7. It has 16 bits, and it is distributed like this

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 11 | 13 | 14 | 15 | 16 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| high fuel level |  |  |  | low fuel level |  |  |  | high battery voltage |  |  |  | low battery voltage |  |  |  |

Now you have to read the values in the register and look to the below table

Ex : if you found in 1 – 4 value 2 = meaning warning alarm

If the value was 3 = meaning shutdown alarm

Page 16 example: Control Registers

This page is used to control the controller and write to module.

I will share the steps with you in modscan, so you can follow by your own.

- Make sure your laptop is communicating with the module via communication cable.

- Open the modscan software and communicate with the module.

- To do remote control (SYSTEM CONTROL) you need to send both System Control Keys to the module, and sending the bitwise opposite (or one’s compliment)

(System Control Keys+ compliment)

To do this using modscan please follow these steps:

- Open modscan

- From TAP menu select SETUP

- From SETUP menu select EXTENDED

- From EXTENDED menu select PRESET REGs

As below :

- You will open the below window (number of points should be 2)

- You will open another window as below

Once you click Update, the mode in the module will change.

EX: to change from Stop to Auto

Select Auto Mode

| Auto Mode | System Control Key (decimal) | Compliment of Control Key |
| --- | --- | --- |
| decimal | 35701 | 29834 |
| Hex | 8B75 | 748A |

Select Stop Mode

| Stop Mode | System Control Key (decimal) | Compliment of Control Key |
| --- | --- | --- |
| decimal | 35700 | 29835 |
| Hex | 8B74 | 748B |

Lock the User Controls

| Lock the User Controls | System Control Key (decimal) | Compliment of Control Key |
| --- | --- | --- |
| decimal | 35736 | 29799 |
| Hex | 8B98 | 7467 |

Unlock the User Controls

| UnLock the User Controls | System Control Key (decimal) | Compliment of Control Key |
| --- | --- | --- |
| decimal | 35737 | 29798 |
| Hex | 8B99 | 7466 |

Page 13 example: digital output

Below Example page 13 , register offset 17 ( for DSE 7420 MKII version 7 and later ).

register offset 17 consist of 16 bit

| 16 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Digital Output A status | Digital Output b status | Digital Output c status | Digital Output d status | Digital Output e status | Digital Output f status | Digital Output g status | Digital Output h status | Digital Output i status | Digital Output j status | Digital Output status | Digital Output status | Not used | Not used | Not used | Not used |

Page 191 example: virtual output

To read a specific alarm, you can configure that on a Virtual Output then read it from GenComm Page 191

You can configure the Virtual LED to read statuses.

Then to read Virtual LED 1 use address: 48,896 (decimal)

Similarly configure Virtual LED 2 for other status functions if required… and read their registers.